SPECIFICATION

Section 07900

ISO-FLEX FACTORY MOLDED

EXPANSION JOINT SEALING SYSTEM

## PART 1 – GENERAL

  - WORK INCLUDED

The work shall consist of furnishing and installing expansion joints in accordance with the details shown on the plans and the requirements of the specifications.

  - RELATED DOCUMENTS

Drawings and provisions of the contract, including General and Supplementary Conditions apply to this section.

  - QUALITY ASSURANCE

- Work under this section shall be performed by an applicator approved by the manufacturer.  The manufacturer shall evidence in writing that the applicator designated to perform the work is qualified to install the specified systems.

- Prequalification of bidders:  Submit proposed subcontractors to the engineer prior to bid.  Qualification criteria shall include compliance with 1.03-A above.  Specifier retains absolutely the right to reject any applicator or manufacturer submitted.

- A site inspection shall be made by the approved applicator prior to commencing installation of the specified system, for the purpose of reviewing related conditions affecting performance requirements of this specification.

- All products described in this section must be used with adequate personal protection.  Refer to the Material Safety Data Sheet that accompanies each product shipment for detailed health and safety information prior to use.

  - SUBMITTALS

- A detailed statement describing the expansion joint sealing system to be installed including typical cross section details with pertinent dimensioning.  Approved Installers shall prepare and submit details of all special conditions to the manufacturer for review and approval prior to installation.

- Manufacturer’s written acceptance and approval of the intended system applicator is required.

## PART 2 – PRODUCTS

  - MATERIALS

- Provide watertight expansion joint sealing system that is capable of accommodating movement caused by thermal expansion and contraction of the substrate.  The system shall be composed of a premolded, two part urethane seal cured to standard dimensions under factory controlled climatic conditions, a one or two part urethane bedding material, an aluminum traffic plate and a two part, high durometer urethane nosing material.

The urethane seal shall be sized to accommodate the total range of movement as dictated by the specifier at each joint location.  Sizing shall be done in such a way as to ensure that the premolded seal will never exceed its maximum movement capability.

Furnish the Iso-Flex Factory Molded Expansion Joint Sealing System type “TS” at locations requiring watertightness, as manufactured by LymTal Intl., and as indicated on the drawings.

  - COMPONENT PROPERTIES

- Factory Molded Seal

Provide seal as specified and indicated on the contract drawings.  Prior to shipment from the factory, the edges of the seal element must be abraded clean.  Seal material shall meet the following physical properties indicated below:

### PHYSICAL PROPERTIES – FACTORY MOLDED SEAL

Physical Properties		ASTM Test Method		Requirements

Shore A Hardness			D-661  			30 +- 5

Tensile Strength			D-412				250 psi

Ultimate Elongation		D-412				700%

Movement Capability		C-719				± 16%

Low Temperature			D-1790			Pass

(Flexibility @ -40º F)

Service Temperature Range					-40ºF to 150ºF

- Polymeric Nosing Material

### PHYSICAL PROPERTIES – POLYMERIC NOSING

Physical Properties		ASTM Test Method		Requirements

Shore A Hardness			D-661  			55 +- 5

Movement Capability		C-719				± 12.5%

Tensile Strength			D-412				1000 psi

Ultimate Elongation		D-412				200%

Weight Loss, Heat Aging		C-792				<5%

Peel Adhesion – Concrete		C-794				50 lbs

Cure Time @ 70( F		C-920				24 hours

Low Temperature Flexibility	D-1790			Pass

C.  Bedding Material

PHYSICAL PROPERTIES – BEDDING MATERIAL

Physical Properties		ASTM Test Method		Requirements

Shore A Hardness			D-661  			30 +- 5

Movement Capability		C-719				± 25%

Tensile Strength			D-412				300 psi

Ultimate Elongation		D-412				600%

Heat Aging			C-920				6%

Recovery				C-920				98%

Cure Time @ 70( F		C-920				24 hours

Low Temperature Flexibility	D-1790			Pass

D.  Primer

All concrete that will come in contact with the Bedding or the Polymeric Nosing must be primed with Iso-Flex Primer #10.

- Traffic Plate

All traffic plates must be made of 6061 T-6 aluminum and be of sufficient width and thickness to accommodate anticipated traffic types and volumes at the widest joint opening dimension.

PART 3 – EXECUTION

  - General

All work shall be installed in strict accordance with the system manufacturer’s recommendations employing trained installers utilizing proper tools and equipment and working under the direct supervision of a technically competent and experienced supervisor.

  - Preparation

- The contractor shall provide properly formed, solid blockouts with clean, sound concrete free of voids and honeycombs, and in accordance with the dimensions detailed in the drawings.

- The contractor shall clean the concrete blockout of all contaminants by sandblasting immediately prior to Iso-Flex Primer #10 installation.  Concrete form release agents, laitance, surface dirt and rust, old sealants and other surface treatments, as well as anything which would inhibit the bond of Iso-Flex 881 Bedding or the 980 Polymeric Nosing must be removed from the blockout surface prior to beginning the installation of the system.

- Areas adjacent to the joint must be masked with tape to assure clean joint lines.

- The blockout area must be completely dry for the application of the Iso-Flex Primer, Bedding or Polymeric Nosing material.  Concrete must be fully cured (28 days) prior to placement of the system.  Blockouts requiring the use of patching compounds must be cured for 72 hours prior to placement of the Iso-Flex system.

- The blockouts must be made to the dimensions and elevations shown on the standard system drawings.  Deviations from these dimensions will not be allowed without the written consent of LymTal Intl.

- The premold seal element shall be unpackaged and laid in a relaxed position to relieve any temporary coiling from shipment packaging prior to placement; the edges of the gland element shall be lightly abraded with a hand grinder/wire wheel attachment then wiped with an acceptable non-petroleum solvent cleaner such as Xylol (Xylene).

- Work shall not proceed under adverse weather conditions or when temperatures are outside the manufacture’s recommended ranges.

  - Installation

The installation of the expansion joint system shall be completed in strict accordance with the manufacturer’s recommendations.

  - Clean and Protect

Protect the Iso-Flex Factory Molded Expansion Joint Sealing System during construction.  Heavy construction vehicles will not be permitted to cross the joint without specific and written permission by the engineer.  Sub sequential damage to the expansion joint system shall be repaired at the contractor’s expense.

-end-